Consumer Confidence Report

OUR WATER

A Water Quality Report for the Water Users of City of Shelby Water Department

Date report was completed:  March 26, 2025

In compliance with the 1996 Safe Drinking Water Act Amendments City of Shelby Water Department is providing our water users with this report on the quality of our drinking water.  This report presents data compiled during the past twelve months from January 1, 2024 to December 31, 2024.

##### Terms and Definitions

| AL | = Action Level, the concentration of a contaminant which triggers treatment or other requirement which a water system must follow |
| --- | --- |
| MCL | = Maximum Contaminant Level, the highest allowable amount of a contaminant that is allowed in drinking water |
| MCLG | = Maximum Contaminant Level Goal, the level of a contaminant in drinking water below which there is no known or expected risk to health |
| ppm | = parts per million, or milligrams per liter (mg/l) |
| ppb | = parts per billion, or micrograms per liter (g/l) |
| TT | = Treatment Technique |
| Variances and Exemptions | = Permission granted by the State not to meet an MCL or treatment technique under certain conditions |
| Treatment Technique | = A required process intended to reduce the level of a contaminant in drinking water |

##### You Should Know

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune disorders, some elderly and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  EPA/CDC guidelines on appropriate means to lessen risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

##### Did You Know?

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban storm water runoff, and septic systems.

- Radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, EPA prescribes regulations which limit the amount of certain contaminants in water provided by public water systems. FDA regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency's Safe Drinking Water Hotline (800-426-4791).

##### Our Water Source

Our water comes from 13 groundwater wells located 7 miles south of the City of Shelby, Montana, in Township 31 North, Range 2 West, Section 21:  S1/2SW1/4, SW1/4SE1/4.  It is pumped to the 4 city water tanks through one 16” water line.

##### Treatment

Our system is presently required to treat its water with UV.

##### Source Water Assessment

A Source Water Assessment will be performed by the State to determine our water system’s susceptibility to contaminants. When the assessment is completed and becomes available, we will make it available to our users.  The State will also make available a brief summary of the susceptibility of the system.  http://deq.mt.gov/Portals/112/water/wpb/NrisReports/Mt0000328.pdf

##### Bacteriological Monitoring

Bacteriological monitoring is performed monthly to test for the presence of coliform bacteria, fecal coliform and E. coli. Our system is required to collect 4 samples per month.

##### Lead and Copper Monitoring

Date Last Sampled for Lead:  September 19th, 2023

90th Percentile for Lead:  less than 2 ppb (Action level = 15 ppb)

Number of Sites Exceeding Lead Action Level:  0

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. The City of Shelby is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using the water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing materials, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at http://www.epa.gov/safewater/lead.

Date Last Sampled for Copper:  September 19th, 2023

90th Percentile for Copper:  .179 MG/L (Action level = 1.3 MG/L)

Number of Sites Exceeding Copper Action Level:  0

##### Chemical Monitoring

Note to our water users: The state requires us to monitor for certain contaminants less often then once per year because the concentrations of these contaminants are not expected to vary significantly from year to year.  Some of our data, such as organic contaminants, though representative, is more than one year old.

### VOCs (Volatile Organic Chemicals) – 19 Regulated, 7 Unregulated

Our sampling detected the presence of:  No detects

Required Sampling Frequency:  Once every three (3) years.

Date Last Sampled:  December 18th, 2022

### SOCs (Synthetic Organic Chemicals) – 27 Regulated, 10 Unregulated

Our sampling detected the presence of:  No detects

Required Sampling Frequency:  Once every three (3) years.

Date Last Sampled:  December 18th, 2022

### IOCs (Inorganic Chemicals)

See Table E - Detected Regulated Inorganic Chemicals.  See Table F – Detected Unregulated Inorganic Chemicals.

Required Sampling Frequency:   Waivered

Date Last Sampled:  August 8, 2017

### Radionuclides

Our sampling detected the presence of:  No detects

Required Sampling Frequency:  Once every nine (9) years.

Date Last Sampled:  August 8, 2017

##### Additional Information

If you would like additional information regarding our water system, feel free to contact:

## Eric Kary

## Public Works Director

## 50 City Shop Road

Shelby, MT 59474	434-5564

The Shelby City Council meets on the first and third Mondays of each month at 6:30 p.m. at the:

Shelby City Council Chambers

112 1st Street South

Shelby, MT 59474

Public meetings are held occasionally to address water and sewer issues throughout the year.  Watch the Shelby Promoter for more information

Table E

Detected Regulated IOCs (Inorganic Chemicals)

| Regulated IOCs |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Detected Contaminate | Sample Date | Lowest Detected Level | Highest Detected Level | MCL | MCLG | Average | Violation (Yes or No) | # Period of Violation | Likely Source* |
| Fluoride | 12-18-22 | .3 MG/L | .3 MG/L | 4 PPM | 4 PPM | .3 MG/L | No | N/A | N/A |
| Nitrates as N | 12-2-24 | .04 MG/L | .4 MG/L | 10 PPM | 10 PPM | .4 MG/L | No | N/A | N/A |

Fluoride Likely Source – Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories

Nitrate Likely Source- Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits

Corrective Steps Taken:  None required.

Table F

Detected Unregulated IOCs (Inorganic Chemicals)

| Detected Contaminant | Sample Date | Highest Detected Level | Lowest Detected Level | Average | Significance of Results |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Alkalinity | 2/17/99 | 238 MG/L | 238 MG/L | 238 MG/L | No known health risk, and not due to be regulated. |  |  |
| Calcium | 7/7/08 | 152 MG/L | 152 MG/L | 152 MG/L | “ “ “ “ “ |  |  |
| Magnesium | 7/7/08 | 28 MG/L | 28 MG/L | 28 MG/L | “ “ “ “ “ |  |  |
| Hardness | 7/7/08 | 498 MG/L | 498 MG/L | 498 MG/L | “ “ “ “ “ |  |  |
| PH | 2/17/99 | 7.5 Units | 7.5 Units | 7.5 Units | “ “ “ “ “ |  |  |
| Conductivity | 2/17/99 | 729 UMHOS | 729 UMHOS | 729 UMHOS | “ “ “ “ “ |  |  |
| Sodium | 2/17/99 | 16 MG/L | 16 MG/L | 16 MG/L | “ “ “ “ “ |  |  |
| Chloride | 2/17/99 | 1 MG/L | 1 MG/L | 1 MG/L | “ “ “ “ “ |  |  |
| Iron | 2/17/99 | <0.03 MG/L | <0.03 MG/L | <0.03 MG/L | “ “ “ “ “ |  |  |
| Manganese | 10/1/24 | .224 MG/L | .014 MG/L | .079 MG/L | “ “ “ “ “ |  |  |
| Lithium | 7/24/24 | 11 ug/L | 11 ug/L | 11 ug/L |  |  |  |
| Sulfate | 10/24/96 | 180 | 180 | 180 | Proposed to be regulated. |  |  |
| These unregulated IOCs generally pose no health risk and are indicators of the quality of the water. |  |  |  |  |  |  |  |

Table G

Detected Radionuclides Inorganic Chemicals)

| Detected Radionuclides |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Detected Contaminant | Sample Date | Lowest Detected Level | Highest Detected Level | MCL* | MCLG* | Average | Violation (Yes or No) | Period of Violation |  |
| Combined Radium 226/238 | 8/8/17 | 1.9 | 1.9 | 0 | 5 | 1.9 pCi/L | NO | N/A |  |
| Uranium | 8/8/17 | 1 | 1 | 0 | 30 | 1 Ug/L | No |  |  |

Table H

Bacteriological Contaminants: Coliform Positive Samples

(If your system is required to do less than 40 samples per month write the number of coliform positive samples for each month in the table in the worksheet. If your system is required to do 40 or more samples per month, write the percentage of coliform positive samples for each month in the table in the worksheet.)

| Coliform Positive Samples |  |  |  |
| --- | --- | --- | --- |
| Date | Positive Samples | Period of Violation | Likely Source |
| 8-5-2024 | 1 |  | Bad Sampling– Retook 9 samples (all came back negative) |

MCLG: 0

MCL: Presence of coliform in 5% of monthly samples, or if a routine sample and a follow up repeat sample are total coliform positive and one is fecal coliform or E. coli positive.

POTENTIAL HEALTH EFFECTS:  Total Coliform. Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other potentially-harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems.

CORRECTIVE STEPS TAKEN:   We resampled 9 sites in the distribution system (1 upstream, 1 downstream, 1 at source of negative sample, and 6 at wells.  All 9 came back negative (8-12-24)